## UT-Report
4253-97 Street, Edmonton AB, T6E 5Y7 Tel.: (780) 417-0340 Fax: (780) 417-0348 www.integrity-testing.com
ULTRASONIC EXAMINATION REPORT | [38 empty] | REPORT No.: | [5 empty] | UT |  |  | - | 1828 |  |  |  | - |  | 003 |  | - | MAJ
[44 empty] | Page: | [6 empty] | 1 |  |  | of |  | 4
| Client: | [7 empty] | Taqa North | [29 empty] | ITS Job No.: |  |  |  |  | 1828
| District: | [7 empty] | Northern | [17 empty] | LSD: |  |  | C-32-H / 94-H-08 | [8 empty] | Date: |  |  |  |  | 2012-07-16
| Facility: | [7 empty] | Chinchaga Gas Plant | [29 empty] | Time: |  |  |  |  | 15:30
| Item(s) Examined: | [7 empty] | Heater Boiler | [29 empty] | W.O. No.: |  |  |  |  | N/A
[39 empty] | P.O. No.: |  |  |  |  | N/A
| Acceptance Criteria: | [7 empty] | Record Low Readings And Anomalies | [17 empty] | Rev. / Date: | [5 empty] | N/A | [5 empty] | Cost Code: |  |  |  |  | N/A
| Procedure No.: | [7 empty] | ITS-UT02 | [17 empty] | Rev. / Date: | [5 empty] | Rev. 1 / Oct-11 | [5 empty] | AFE: |  |  |  |  | 11200624
| Technique No.: | [7 empty] | Technique 01 | [17 empty] | Rev. / Date: | [5 empty] | Rev. 1 / Oct-11 | [5 empty] | Other: |  |  |  |  | N/A
Equipment Data:
| PRN: |  |  |  | N/S | [9 empty] | Serial No.: |  |  | 06-274 | [10 empty] | Equip. No.: |  |  |  |  | 603FB001 | [6 empty] | CRN: |  |  | K-6154.12
A
| Material: |  |  |  | N/S | [17 empty] | Thickness: |  |  |  |  | N/S | [10 empty] | Other: |  | N/S
Surface Condition:
[47 empty] | Other: |  |  |  | N/A
|  | Base Metal | [5 empty] | Machined | [5 empty] | Shot Blasted | [7 empty] | Wire Wheeled | [6 empty] | As Ground | [6 empty] | As Welded |  |  | Painted |  |  |  | Coated
|  | < 0°C (32°F) | [11 empty] | 0°C (32°F) to 54°C (130°F) | [16 empty] | 55°C (131°F) to 100°C (212°F) | [14 empty] | > 100°C (212°F)
Ultrasonic Equipment:
| Instrument: |  |  |  |  | Krautkramer | [10 empty] | Model: |  |  |  | USN 58L | [9 empty] | Serial No.: |  |  |  |  | O1P514 | [6 empty] | Cal. Due Date: | [6 empty] | 2013-01-09
| Cal. Block: |  |  |  |  | 2.5-12.5mm Step Wedge | [24 empty] | Serial No.: |  |  |  |  | 555109 | [6 empty] | Couplant: | [6 empty] | UTX
| Cal. Block: |  |  |  |  | N/A | [24 empty] | Serial No.: |  |  |  |  | N/A
| Transducer Cable(s); | [9 empty] | Type: | BNC - Micro Dot | [18 empty] | Length: |  |  |  |  | 6'
Transducer:
| Serial No.: | [5 empty] | Angle (X°): |  |  |  | Frequency (MHz): |  |  |  |  | Size (mm): |  |  |  | Type | [5 empty] | Primary Reference (db) (%FSH): | [10 empty] | Scanning Sensitivity (db): |  |  |  |  | Transfer Value (db): | [9 empty] | Range (mm):
[20 empty] | Single |  |  | Dual
| 705183 | [5 empty] | 0 |  |  |  | 10 |  |  |  |  | 6.375 | [9 empty] | 48dB @ 80% FSH | [10 empty] | +6dB to maintain 80% FSH |  |  |  |  | N/A | [9 empty] | 0-25
Examination Details:
Client Representative: | [27 empty] | Sign: | [17 empty] | Date:
Technician(s):
Sign:
| Print: |  |  | Mike Johnston | [19 empty] | Rob Kassian | [17 empty] | Report Review:
|  |  |  | 1st Technician | [19 empty] | 2nd Technician / Assistant | [23 empty] | Initial
[10 empty] | CGSB |  |  | SNT |  |  |  | ACCP/ASNT | [12 empty] | CGSB |  |  |  |  | SNT |  |  | ACCP/ASNT
[5 empty] | Level: |  |  |  |  | 2 | [14 empty] | Level:
[5 empty] | Certification No.: |  |  |  |  | 12240 | [14 empty] | Certification No.: |  |  |  |  | 15532
Scope of Services The agreement of Integrity Testing Services Inc. to perform services extends only to those services provided for in writing. Under no circumstances shall such services extend beyond the performance of the requested inspection of specific equipment provided for in writing and the preparation of reports or similar documents reflecting the inspection data obtained or the opinion formulated on the basis of such inspection. It is expressly understood that all descriptions, comments and expressions of opinion reflect the opinion or observations of the examiner and are not intended nor can they be construed as representations or warranties as to the actual circumstances. ITS is not assuming any responsibilities of the owner/operator, and the owner/operator retains complete responsibility for the engineering, repair and use decisions as a result of the inspection data or other information provided by ITS. In no event shall ITS’s liability in respect of the services referred to herein exceed the amount paid for such services. Standard of Care In performing the services provided, Integrity Testing Services Inc. uses the degree, care and skill ordinarily exercised under similar circumstances by others performing such services in the same or similar locality. No other warranty, expressed or implied, is made or intended by ITS.
CONTINUATION EXAMINATION REPORT | [38 empty] | REPORT No.: | [5 empty] | UT |  |  | - | 1828 |  |  |  | - |  | 003 |  | - | MAJ
[44 empty] | Page: | [6 empty] | 2 |  |  | of |  | 4
Client: | [8 empty] | Taqa North | [29 empty] | ITS Job No.: |  |  |  |  | 1828
Item(s) Examined: | [8 empty] | Heater Boiler | [29 empty] | Date: |  |  |  |  | 2012-07-16
1st Technician:
| Print: |  | Mike Johnston | [26 empty] | Sign:
CONTINUATION EXAMINATION REPORT | [38 empty] | REPORT No.: | [5 empty] | UT |  |  | - | 1828 |  |  |  | - |  | 003 |  | - | MAJ
[44 empty] | Page: | [6 empty] | 3 |  |  | of |  | 4
Client: | [8 empty] | Taqa North | [29 empty] | ITS Job No.: |  |  |  |  | 1828
Item(s) Examined: | [8 empty] | Heater Boiler | [29 empty] | Date: |  |  |  |  | 2012-07-16
1st Technician:
| Print: |  | Mike Johnston | [26 empty] | Sign:
| Wraps | [5 empty] | 12 O'clock | [11 empty] | 3 O'clock | [12 empty] | 6 O'clock | [7 empty] | 9 O'clock
| 1 EAST | [5 empty] | 5.7 | [11 empty] | 5.6 | [12 empty] | 5.6 | [7 empty] | 5.8
| 2 | [5 empty] | 5.6 | [11 empty] | 5.7 | [12 empty] | 5.7 | [7 empty] | 5.8
| 3 | [5 empty] | 5.4 | [11 empty] | 5.8 | [12 empty] | 5.7 | [7 empty] | 5.7
| 4 | [5 empty] | 5.7 | [11 empty] | 5.8 | [12 empty] | 5.8 | [7 empty] | 5.6
| 5 | [5 empty] | 5.8 | [11 empty] | 5.9 | [12 empty] | 5.7 | [7 empty] | 5.7
| 6 | [5 empty] | 5.6 | [11 empty] | 5.8 | [12 empty] | 5.8 | [7 empty] | 5.8
| 7 | [5 empty] | 5.7 | [11 empty] | 5.9 | [12 empty] | 5.7 | [7 empty] | 5.8
| 8 | [5 empty] | 5.6 | [11 empty] | 6 | [12 empty] | 5.8 | [7 empty] | 5.6
| 9 | [5 empty] | 5.8 | [11 empty] | 5.9 | [12 empty] | 5.7 | [7 empty] | 5.8
| 10 | [5 empty] | 5.7 | [11 empty] | 5.8 | [12 empty] | 5.5 | [7 empty] | 5.2
| 11 | [5 empty] | 5.6 | [11 empty] | 5.8 | [12 empty] | 5.5 | [7 empty] | 5.6
| 12 | [5 empty] | 5.5 | [11 empty] | 5.8 | [12 empty] | 5.6 | [7 empty] | 5.6
| 13 | [5 empty] | 5.5 | [11 empty] | 5.7 | [12 empty] | 5.7 | [7 empty] | 5.5
| 14 | [5 empty] | 5.8 | [11 empty] | 5.7 | [12 empty] | 5.7 | [7 empty] | 5.9
| 15 | [5 empty] | 5.5 | [11 empty] | 5.8 | [12 empty] | 5.8 | [7 empty] | 5.3
| 16 | [5 empty] | 5.6 | [11 empty] | 5.6 | [12 empty] | 5.6 | [7 empty] | 5.6
| 17 | [5 empty] | 5.5 | [11 empty] | 5.6 | [12 empty] | 5.7 | [7 empty] | 5.4
| 18 | [5 empty] | 5.7 | [11 empty] | 6 | [12 empty] | 5.5 | [7 empty] | 5.8
| 19 | [5 empty] | 5.8 | [11 empty] | 5.7 | [12 empty] | 5.5 | [7 empty] | 5.8
| 20 | [5 empty] | 5.8 | [11 empty] | 5.7 | [12 empty] | 5.7 | [7 empty] | 5.7
| 21 | [5 empty] | 5.8 | [11 empty] | 5.8 | [12 empty] | 5.6 | [7 empty] | 5.7
| 22 | [5 empty] | 5.8 | [11 empty] | 5.7 | [12 empty] | 5.6 | [7 empty] | 5.7
| 23 | [5 empty] | 5.7 | [11 empty] | 5.8 | [12 empty] | 5.8 | [7 empty] | 5.7
| 24 | [5 empty] | 5.7 | [11 empty] | 5.7 | [12 empty] | 5.6 | [7 empty] | 5.6
| 25 | [5 empty] | 5.7 | [11 empty] | 5.8 | [12 empty] | 5.6 | [7 empty] | 5.6
| 26 | [5 empty] | 5.8 | [11 empty] | 5.7 | [12 empty] | 5.8 | [7 empty] | 5.6
| 27 | [5 empty] | 5.8 | [11 empty] | 5.8 | [12 empty] | 5.9 | [7 empty] | 5.6
| 28 | [5 empty] | 5.8 | [11 empty] | 5.9 | [12 empty] | 5.9 | [7 empty] | 5.8
| 29 | [5 empty] | 5.7 | [11 empty] | 6 | [12 empty] | 5.7 | [7 empty] | 5.7
| 30 | [5 empty] | 5.6 | [11 empty] | 6 | [12 empty] | 5.7 | [7 empty] | 5.7
| 31 | [5 empty] | 5.8 | [11 empty] | 5.8 | [12 empty] | 5.8 | [7 empty] | 5.7
| 32 | [5 empty] | 5.7 | [11 empty] | 5.8 | [12 empty] | 5.9 | [7 empty] | 5.6
| 33 | [5 empty] | 5.8 | [11 empty] | 5.8 | [12 empty] | 5.8 | [7 empty] | 5.6
| 34 | [5 empty] | 5.7 | [11 empty] | 6 | [12 empty] | 5.8 | [7 empty] | 5.8
| 35 | [5 empty] | 5.8 | [11 empty] | 5.8 | [12 empty] | 5.7 | [7 empty] | 5.8
| 36 | [5 empty] | 5.8 | [11 empty] | 5.8 | [12 empty] | 5.6 | [7 empty] | 5.7
| 37 | [5 empty] | 5.8 | [11 empty] | 5.8 | [12 empty] | 5.7 | [7 empty] | 5.4
| 38 | [5 empty] | 5.7 | [11 empty] | 5.6 | [12 empty] | 5.7 | [7 empty] | 5.7
| 39 | [5 empty] | 5.8 | [11 empty] | 5.7 | [12 empty] | 6 | [7 empty] | 5.7
| 40 WEST | [5 empty] | N/A | [11 empty] | 5.8 | [12 empty] | 5.8 | [7 empty] | N/A
Note on CY7: AUTOMATED FIELD, DO NOT FILL.
Note on DG7: nbartley: Incremental number, When using this form as a blanket report start with '00' for a report number.
Note on DK7: nbartley: Technician Initials
SCOPE:
LIMITATIONS:
RESULTS:
CONCLUSION:
To perform an Ultrasonic Thickness survey on 603FB001 Heatec 3" coil. Each wrap was scanned at the 12-3-6-9 O'clock positions in a 3" band along the the accessible area of the exposed coil and the minimum found reading was recorded. The coil is numbered as # one to the East and # forty to the West.
Only 100° of the coil was available to scan.
There were no concerns identified in the examined areas. See readings below for more details. The lowest found area was on coil #10 which had a reading of 5.2 mm.
This vessel, based on the scope and acceptable criteria of the heater coil, is a recommended fit for return to service.
AUTOMATED SECTION, DO NOT FILL.
AUTOMATED SECTION, DO NOT FILL.
NORTH
NORTH
NORTH
NORTH
3" 90* Elbow 5.3mm
3" 45* Elbow 5.3mm
3" 90* Elbow 5.4mm